REFERENCE: RFP 63/2018

SCOPE OF WORK

APPOINTMENT OF A SUITABLY QUALIFIED GENERAL CONTRACTOR (CIDB GRADE 2 GB OR HIGHER) TO MAKE CHANGES TO THE FIRE ESCAPE DOORS AND WINDOWS AT LEHAE LA SARS FOR ALL FLOORS OF BLOCK A & D ONLY

- INTRODUCTION

The Lehae La SARS is situated at 299 Bronkhorst Street, Nieu Muckleneuck, Pretoria. The campus, as it is called, consists of eight buildings. The work is required at Block A and Block D (refer to the architectural drawings of each floor). Six existing aluminium frame fire doors and windows need to be replaced with doors and windows of steel frames and 30 minutes fire resistant Georgian wired glass. Also refer to the bill of quantities.

- SCOPE

The services of a construction contractor is required to carefully remove the six existing fire escape doors and windows in Block A and Block D, ground-, 1st- and second floor. The existing doors and windows needs to be carefully removed by demolishing the brickwork around it, removing the doors and windows and remove it via the fire escape stairs to ground floor level.

It is for this reason that an Occupational Health and Safety policy and plan is required from the contractor. The plan should include for example what the successful contractor will put in place to ensure the safety of his workers while using the fire escape stairs. The lifts inside the buildings will be out-of-bounds for the contractor.

The contractor will be required to re-install the newly acquired steel frame-doors and windows with Georgian fire rated glass to withstand fire for up to 30 minutes. This will assist with the vacating of personnel from the building in an event of a fire. The openings (doors and windows) have to be bricked up again with the same standard of bricks as the existing, plastered, painted and all areas, including the carpets, needs to be properly cleaned immediately after each construction session. All building rubble must be removed directly the work has been completed.

The doors and windows will have to be ordered in advance from a specialised supplier specialising in fire rated glass and doors and windows. The expected lead time from placing an order and manufacturing may take up to 12 weeks. This exclude the December builder’s holidays.

Each fire escape route has a small step leading to the outside steel fire escape stairs. To ease the vacating of the buildings a steel ramp needs to be manufactured and installed to eliminate the height difference of the step. Details of the ramps are included in the Ramp Rev1–Ramp detail drawing.

- CONCLUSION

A certificate of compliance will be required from the contractor after the works have been completed. Details of the doors and windows are included in the “Doors and Window Schedule”. At the completion of the project the fire doors and windows for all floors in Block A and Block D including the elimination of the step will comply with the Fire Department requirements.

The buildings will be fully occupied during construction and no work is allowed on electrical systems without prior approval.

- INSURANCE REQUIREMENTS

HOT WORK OPERATIONS

It is noted that operations include employees working on Third Party premises installing closures, locks etc.  It is understood that on an occasional basis ‘Hot Work’ is performed.

The use of gas or electric welding/cutting apparatus plus blow lamps/torches, have resulted in numerous fires.  Costs running into millions of pounds are not uncommon.  Prior to any such equipment being used on a premises, other than in purpose-designed areas, careful thought should be entered into.  The ‘Hot Work Permit’ is intended to ensure that the hot work process is properly managed.

The Insured should introduce a procedure requiring all Hot Work to be controlled by a Hot Work Permit and associated procedures see Appendix.

HOT WORK AWAY

Hot Work shall include but not be limited to the use of gas and electrical powered welding burning or cutting equipment blow lamps and blow torches grinding equipment and vessels for heating of bitumen or bitumus compounds

The Hot Work Area shall mean an area of space within a 10 metre radius vertically as well as horizontally of any Hot Work where such Hot Work involves any use of gas and electrical powered welding burning or cutting equipment.

In respect of other Hot Work the Hot Work Area shall mean an area of space within a 3 metre radius vertically as well as horizontally of such work.

Precautions applicable to all Hot Work away from any premises owned leased or rented by the Insured

1	Before Hot Work is commenced the occupier of the premises must be informed of the proposed safety precautions and asked for specific authority to proceed and a Hot Work Permit completed either in the form attached at Appendix A or in a similar form provided by the occupier provided always that the completion of the Hot Work Permit shall not vary or waive any of the undertakings or conditions precedent contained herein.

2	The Hot Work Area is to be cleared of loose or exposed combustible or flammable material or liquids.  If such combustible material or liquids 	cannot be removed they should be protected with flameproof covers. Floors, walls, ceilings, roofs, ducts and partitions made of combustible material are also to be protected with flameproof covers.

Openings in floors, walls, ceilings, roofs or ducts within the Hot Work Area are to be closed, covered sealed or otherwise rendered impervious to the passage of air.

3	Before applying heat to metal or other conducting material which is built into or projects  through walls, partitions, cavities, ceilings, or floors, roofs or ducts an  examination is to be made to ensure that there is no combustible material in hazardous proximity to such metal or conducting material which may be ignited by direct or conducted heat.

4	No Hot Work is to be carried out :

(a) in atmospheres which are potentially explosive through the presence of vapours or dusts; or

(b)  in areas where flammable fluids and/or flammable materials are not totally enclosed or   where processes incorporating the same are not shut down; or

(c)  on metal or other conducting materials in contact with combustible walls, partitions, cavities, ceilings, floors, roofs or ducts if close enough to cause ignition by conduction or direct heat.

5	Throughout the period of Hot Work and throughout the period of examination after termination of work referred to in precaution 8 a fire extinguisher of a suitable capacity and type having regard to area at risk shall be kept available for immediate use.

6	All persons engaged in the Hot Work  shall be made aware of the location of all fire fighting equipment.

Where the Hot Work involves any use of gas and electrical powered welding burning or cutting equipment a responsible employee of the Insured or of the Occupier of the premises shall be appointed to act solely as fire prevention officer/fire watcher and is to be present at all times when  Hot Work is carried out.

- The Insured must ensure that all fire protection controls remain effective during the period of Hot Work Such fire protection controls are to include but not be limited to, fire doors being  closed, sprinkler systems  remaining operable and ventilation to prevent formation of explosive atmospheres remaining  operable.

8	The Insured must ensure that a thorough examination is made in and about the Hot Work Area including behind walls, partitions, ceilings, roofs or floors, during operations.  The same examination is to be continuously carried out for a minimum of 60 minutes after any termination of any Hot Work before the Hot Work Area can be left unattended by the Insured.

9	Hot Work equipment, when lit, or naked flames shall never be unattended for any period of time.

10 	Blow Lamps and Blow Torches shall only be filled in the open.

11	Vessels for heating of bitumen or bituminous compounds shall only be used in the open and shall be continuously attended whilst heating is taking place.

12	Without prejudice to the generality of any the foregoing the Insured shall take all reasonable care to prevent accidents and act in accordance with all generally accepted safe working practices and all applicable statutory obligations and regulations.

HOT WORK PERMIT

ISSUING COMPANY 					  PERMIT NO.

A	PROPOSAL  (To be completed by the person responsible for carrying out the work)

BUILDING

EXACT LOCATION OF PROPOSED WORK

NATURE OF HOT WORK TO BE UNDERTAKEN

The above location has been examined and the precautions listed on the reverse side of this form have been complied with as indicated.

SIGNED  				  NAME (BLOCK CAPITALS)

DATE  					  POSITION

CONTRACTOR (WHERE APPLICABLE)

B	AGREEMENT  (To be completed by the company fire officer or other nominated person)

This Hot Work Permit is issued subject to the following conditions:

TIME OF ISSUE OF PERMIT  			  TIME OF EXPIRY OF PERMIT

A FINAL FIRE CHECK OF THE WORK AREA SHALL BE MADE, NOT BEFORE

ADDITIONAL CONDITIONS REQUIRED:-

SIGNED  				  NAME (BLOCK CAPITALS)

DATE  					  POSITION

CONTRACTOR (WHERE APPLICABLE)

C	FIRE WATCH  (To be completed by member of staff or contractor responsible for the work before returning this permit to the issuer)

The work area and all adjacent areas to which sparks and heat might have spread (such as floors below and above, and areas on other sides of walls) have been inspected and found to be free of fire following completion of the work.

TIME INSPECTION COMPLETED  			  (This must be at least 1 hour after work was completed)

SIGNED  				  NAME (BLOCK CAPITALS)

DATE  					  POSITION

CONTRACTOR (WHERE APPLICABLE)

*  It is not desirable to issue permits for protracted periods.  Fresh permits should be issued, for example, where work extends from morning to afternoon.

NB   Where work is being carried out by a contractor, the issuer of the permit should ensure that the contractor has complied with the requirements prior to work being carried out, and should be satisfied that the area is free of fire when work is completed.